## Slide 1
VuePoint Eye Comfort Study
Brad Thomas | 11/06/19

## Slide 2: Eye Comfort Concept
The concept behind this test is that eye comfort is affected by three things
  The luminous intensity
    i.e. a 70,000 lumen light will hurt your eyes whether it is 2mm or 1m in diameter
    This is not a parameter we can change because we must build luminaires at certain lumen levels
  The size and contrast of pixilation within the light emitting area
    A large diffuse light source is easy on the eyes, as long as it is not too bright
    The same lumen output compacted into a smaller and smaller number of brighter and brighter spot sources with dark between them is uncomfortable to the eyes
    This we have control over!
  Patterns visible within the light emitting surface
    Patterns catch your eye
    Patterns with irregularities are more annoying than uniformity and symmetry
    Irregular gaps like screw heads bother people
    Make patterns as subdued and uniform as possible

## Slide 3: Eye Comfort Equation
The Eye Comfort Equation is based on two factors
  The relative size of the lighted source(s)
    Calculate the solid angle in steradians that the lighted area subtends
      This could be the bare LED, COB, lens, or diffuser area
  The contrast ratio within the light emitting area
    Probe the Radiant Imaging Camera file for the maximum and minimum Luminance within the output area of the light
    The max/min ratio is the luminance contrast (LC)
  The equation: 5/log(LC/Ω)
    LC/Ω gets larger as the contrast goes up and angle goes down
    Log function reduces it from over a billion to a 0-10 scale
    5 over log(LC/Ωm) makes it a full scale of ~10 so that it can be related to the human subject voting on a scale of 5

## Slide 4: Luminance
Luminance is the measure of the amount of light emitted from a surface
  Units are candelas per square meter
  It is light at the source not on the target, so it is independent of distance
  However, to measure it the radiant camera needs to know the lens focal length and distance to the source to calculate the area and therefore the Luminance

## Slide 5: VuePoint with Bare LEDs
LED 8,900,000 to space 2,000 is 4,450:1 ratio over 3mm span
Eye Comfort = 0.55
True Color
Luminance

## Slide 6: VuePoint with Bare LEDs - Luminance Profile
Extreme bright to dark contrast is uncomfortable to the eyes

## Slide 7: VuePoint with Bare LEDs – Light Tools Simulation
LED 4,400,000 to space 800 is 5,500:1 ratio over 3mm span
Eye Comfort = 0.55
Luminance

## Slide 8: VuePoint P1 with Fresnel Lens
LED 3,900,000 to space 3,000 is 1,300:1 ratio over 15mm span
Eye Comfort = 0.59
True Color
Luminance

## Slide 9: Flex without Lens
LED 2,500,000 to space 2,500 is 1,000:1 ratio over 3mm span
Eye Comfort = 0.62
True Color
Luminance

## Slide 10: LEDway with 2M Optics
LED 1,600,000 to space 2,000 is 800:1 ratio over 5mm span
Eye Comfort = 0.67
True Color
Luminance

## Slide 11: KBL-A (external Meanwell driver)
LED 8,300,000 to space 30,000 is 277:1 ratio over 5mm span
Eye Comfort = 0.67
True Color
Luminance

## Slide 12: VuePoint P1 with Diffuser only
LED 1,800,000 to space 2,500 is 720:1 ratio over 15mm span
Eye Comfort = 0.73
True Color
Luminance

## Slide 13: CPY 250 with Flat Lens
LED 1,300,000 to space 30,000 is 43:1 ratio over 6mm span
Eye Comfort = 0.79
True Color
Luminance

## Slide 14: XSP 3ME
LED 9,235,000 to space 45,000 is 205:1 ratio over 30mm span
Eye Comfort = 0.85
True Color
Luminance

## Slide 15: CXB-A
LED 6,000,000 to space 45,000 is 133:1 ratio over 20mm span
Eye Comfort = 0.85
True Color
Luminance

## Slide 16: HXB 70kL Medium Optic at 65° Viewing Angle
LED 1,400,000 to reflector 66,000 is 21:1 ratio over 26mm span
Eye Comfort = 0.95
True Color
Luminance

## Slide 17: RSW Small 2ME (from slightly in front)
Max 7,800,000 to space 8,000 is 975:1 ratio over 75mm span
Eye Comfort = 0.96
True Color
Luminance

## Slide 18: RSW Small (from slightly behind)
Max 393,000 to space 13,000 is 30:1 ratio over 75mm span
Eye Comfort = 1.36
True Color
Luminance

## Slide 19: IG
Max 50,000 to space 1,500 is 33:1 ratio over 125mm span
Eye Comfort = 1.47
True Color
Luminance

## Slide 20: VG with narrow reflector
Max 96,000 to space 4,000 is 24:1 ratio over 150mm span
Eye Comfort = 2.0
True Color
Luminance

## Slide 21: Flex with Lens
LED 46,000 to diffuser edge 5,000 is 9:1 ratio over 100mm span
Eye Comfort = 2.05
True Color
Luminance

## Slide 22: LS4 White Satin Ice at Nadir
LED 16,400 to diffuser edge 9,000 is 1.8:1 ratio over 50mm span
Eye Comfort = 2.14
True Color
Luminance

## Slide 23: VuePoint with Diffuser
Center 36,000 to edge 15,000 is 2.4:1 ratio over 230mm span
True Color
Luminance
Eye Comfort = 3.3

## Slide 24: VuePoint with Diffuser
Center 55,000 to edge 2,000 is 27.5:1 ratio over 230mm span
Eye Comfort = 1.9
Luminance from Light Tools

## Slide 25: VuePoint with Diffuser - Luminance Profile
Gradual intensity transition is comfortable to the eyes

## Slide 26: VuePoint 12kL Scalloped Edge Luminance
Scalloped pattern of intensity is not uncomfortable, but is annoying

## Slide 27: Measurement Method
Radiant image files were probed manually to get a maximum luminance delta in the smallest distance
Numbers entered into the spreadsheet are a nominal high to nominal low, not the absolute max and min
CPY: 1.3M – 30K in 6mm
KBL: 8.3M – 30K in 5mm
KBL: 393K – 13K in 75mm
VuePoint: 36K – 15K in 230mm

## Slide 28: Eye Comfort Formula Graph
Group eye comfort rating is average of scores from:
Brad Thomas, Jon Vollers, Erik Milz, and Randy Bernard

## Slide 29: Data for Eye Comfort Scores
Luminaire | Brad's Eye Comfort Rating (1 bad to 5 good) | Group Eye Comfort Rating (1 bad to 5 good) | Viewing Distance (ft) | Max-Min Separation (mm) | Area (sq ft) | Ω Solid Angle (Steradians) | Maximum Luminance (cd/m^2) | Minimum Luminance (cd/m^2) | Luminous Contrast: LC (Lmax/Lmin) | LC/Ω (luminous contrast / steradian) | Eye Comfort Score (5/log(LC/Ω))
VuePoint with bare LEDs | 1 | 1.33 | 20 | 3 | 0.0000761 | 0.0000038 | 8,900,000 | 2,000 | 4450 | 1.17E+09 | 0.55
VuePoint P1 with Fresnel lens | 1 | 2.00 | 20 | 3 | 0.0000761 | 0.0000038 | 3,900,000 | 3,000 | 1300 | 3.42E+08 | 0.59
Flex Troffer with bare LEDs | 1 | 1.33 | 10 | 3 | 0.0000761 | 0.0000076 | 2,500,000 | 2,500 | 1000 | 1.31E+08 | 0.62
LEDway with 2M NanoOptic | 1 | 1.67 | 30 | 10 | 0.0008454 | 0.0000282 | 1,600,000 | 2,000 | 800 | 2.84E+07 | 0.67
KBL-A with bare small LEDs | 2 | 2.67 | 20 | 5 | 0.0002113 | 0.0000106 | 8,300,000 | 30,000 | 277 | 2.62E+07 | 0.67
VuePoint P1 with diffuser | 2 | 2.50 | 20 | 15 | 0.0019021 | 0.0000951 | 1,800,000 | 2,500 | 720 | 7.57E+06 | 0.73
CPY 250 flat lens | 2 | 2.00 | 15 | 6 | 0.0003043 | 0.0000203 | 1,300,000 | 30,000 | 43 | 2.14E+06 | 0.79
XSP with 3ME lens | 2 | 2.00 | 30 | 30 | 0.0076086 | 0.0002536 | 9,235,000 | 45,000 | 205 | 8.09E+05 | 0.85
CXB with bare COB LEDs | 2 | 1.33 | 20 | 20 | 0.0033816 | 0.0001691 | 6,000,000 | 45,000 | 133 | 7.89E+05 | 0.85
HXB with medium lens | 3 | 2.50 | 50 | 26 | 0.0057149 | 0.0001143 | 1,400,000 | 66,000 | 21.2 | 1.86E+05 | 0.95
RSW-S 2ME from front | 3 | 3.00 | 30 | 150 | 0.1902140 | 0.0063405 | 7,800,000 | 8,000 | 975 | 1.54E+05 | 0.96
RSW-S 3ME from rear | 4 | 4.00 | 30 | 150 | 0.1902140 | 0.0063405 | 393,000 | 13,000 | 30.2 | 4.77E+03 | 1.36
IG with standard lens | 4 | 4.33 | 10 | 125 | 0.1320931 | 0.0132093 | 50,000 | 1,500 | 33 | 2.52E+03 | 1.47
VG with narrow reflector | 4 | 3.67 | 10 | 300 | 0.7608560 | 0.0760856 | 96,000 | 4,000 | 24 | 3.15E+02 | 2.00
Flex Troffer with lens | 4 | 4.33 | 10 | 200 | 0.3381582 | 0.0338158 | 46,000 | 5,000 | 9.2 | 2.72E+02 | 2.05
LS4 with White Satin Lens | 4 | 4.67 | 10 | 100 | 0.0845396 | 0.0084540 | 16,400 | 9,000 | 1.8 | 2.16E+02 | 2.14
VuePoint with diffuser only | 5 | 4.67 | 20 | 406 | 1.394 | 0.070 | 36,000 | 15,000 | 2.4 | 3.44E+01 | 3.25
Perfectly uniform 2' flat panel | 5 | 5.00 | 10 | 609 | 3.135 | 0.314 | 20,000 | 20,000 | 1 | 3.19E+00 | 9.93

## Slide 30
Cylon Study

## Slide 31: CPY 250 with Flat Lens
LED 565,000 to space 20,000 is 28:1 ratio over 6mm span
Eye Comfort = 0.81
True Color
Luminance
Cylon Study

## Slide 32: CPY 250 with Drop Lens
LED 627,000 to space 15,000 is 42:1 ratio over 4mm span
Eye Comfort = 0.75
True Color
Luminance
Cylon Study

## Slide 33: LSI Scottsdale Vertex
LED 1,022,000 to space 10,000 is 102:1 ratio over 4mm span
Eye Comfort = 0.71
True Color
Luminance
Cylon Study

## Slide 34: Jarvis Xbeam
LED 8,000,000 to space 20,000 is 400:1 ratio over 25mm span
Eye Comfort = 0.83
True Color
Luminance
Cylon Study

## Slide 35: Eye Comfort Formula Graph with Cylon Data
Group eye comfort rating is average of scores from:
Brad Thomas, Jon Vollers, Erik Milz, and Randy Bernard